## INSTRUCTIONS
HARSCO Industrial / PATTERSON - KELLEY CSD-1 FORM
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
1 | Complete data below
| a. | from the packing list, enter the serial number |  | XXYY-16-ZZZZZ
| b. | from the H-3 data report, enter the Nat. Bd. number |  | XXXX
| c. | from the serial number, enter the year built |  | 2016
(e.g. - CL52-08-12345 means year built is 2008)
2 | Enter Jurisdiction (usually the state) |  |  | ILLINOIS
3 | Enter installation information
|  |  | Name | EXAMPLE BUILDING
|  |  | Address | 123 MAIN ST
|  |  | City | SPRINGFIELD
|  |  | State | IL
|  |  | Zip | 62701
Phone
Fax
4 | Enter Representative's Company (your) name |  |  | P-K REP CO.
5 | IMPORTANT: Select correct tab (below) for correct model number
6 | The cells for the relief valve are NOT locked so that you can correct for the supplied valve.
7 | Print the "worksheet" for that model ONLY
This workbook will populate ALL models and ALL tabs with the same information - again, only select
and print the worksheet for your specific model.

## W750MFD - NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
HARSCO Industrial, Patterson-Kelley
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-4247
Unit Identification (Boiler)
| Model | W750-MFD | Year Built | 2016
| Nat. Bd. # | XXXX |  | CSA Report # |  | 166908-1612096
| Boiler/Burner Serial Number |  |  | XXYY-16-ZZZZZ
| Jurisdiction |  | ILLINOIS
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 750000 | btu/hr
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Copper, Watertube
| Boiler Unit Capacity (Output) |  |  |  |  | 637500 | btu/hr
| Burner Manufacturer |  |  | HARSCO Industrial / Patterson-Kelley Co.
| Model | W750-MFD |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | EXAMPLE BUILDING
| Adress |  | 123 MAIN ST
| City | SPRINGFIELD |  | State | IL | Zip | 62701
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  | (self contained) | Honeywell |  | RM7910A1183/U
Safety Controls
L.W.C.O., Forced Circulation - CW210 |  |  |  | Johnson |  | F261KAH-V01C
High Water Temperature Limit - CW-410(b) |  |  |  | Jumo |  | EMF-5
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000/257-805
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000/257-805
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.E021180
High Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Low Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Purge Air Flow - CF210 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | C7027A1114(UV)
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20 | (3/4"x 3/4")
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | P-K REP CO.
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | XXYY-16-ZZZZZ

## W1000MFD - NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
HARSCO Industrial, Patterson-Kelley
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-4247
Unit Identification (Boiler)
| Model | W1000-MFD | Year Built | 2016
| Nat. Bd. # | XXXX |  | CSA Report # |  | 166908-1612096
| Boiler/Burner Serial Number |  |  | XXYY-16-ZZZZZ
| Jurisdiction |  | ILLINOIS
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 1000000 | btu/hr
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Copper, Watertube
| Boiler Unit Capacity (Output) |  |  |  |  | 850000 | btu/hr
| Burner Manufacturer |  |  | HARSCO Industrial / Patterson-Kelley Co.
| Model | W1000-MFD |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | EXAMPLE BUILDING
| Adress |  | 123 MAIN ST
| City | SPRINGFIELD |  | State | IL | Zip | 62701
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  | (self contained) | Honeywell |  | RM7910A1183/U
Safety Controls
L.W.C.O., Forced Circulation - CW210 |  |  |  | Johnson |  | F261KAH-V01C
High Water Temperature Limit - CW-410(b) |  |  |  | Jumo |  | EMF-5
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000/257-805
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000/257-805
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.E021180
High Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Low Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Purge Air Flow - CF210 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | C7027A1114(UV)
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20 | (3/4"x 3/4")
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | P-K REP CO.
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | XXYY-16-ZZZZZ

## W1500MFD - NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
HARSCO Industrial, Patterson-Kelley
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-4247
Unit Identification (Boiler)
| Model | W1500-MFD | Year Built | 2016
| Nat. Bd. # | XXXX |  | CSA Report # |  | 166908-1612096
| Boiler/Burner Serial Number |  |  | XXYY-16-ZZZZZ
| Jurisdiction |  | ILLINOIS
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 1500000 | btu/hr
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Copper, Watertube
| Boiler Unit Capacity (Output) |  |  |  |  | 1275000 | btu/hr
| Burner Manufacturer |  |  | HARSCO Industrial / Patterson-Kelley Co.
| Model | W1500-MFD |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | EXAMPLE BUILDING
| Adress |  | 123 MAIN ST
| City | SPRINGFIELD |  | State | IL | Zip | 62701
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  | (self contained) | Honeywell |  | RM7910A1183/U
Safety Controls
L.W.C.O., Forced Circulation - CW210 |  |  |  | Johnson |  | F261KAH-V01C
High Water Temperature Limit - CW-410(b) |  |  |  | Jumo |  | EMF-5
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000/257-805
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000/257-805
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.E021180
High Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Low Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Purge Air Flow - CF210 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | C7027A1114(UV)
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20 | (3/4"x 3/4")
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | P-K REP CO.
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | XXYY-16-ZZZZZ

## W2000MFD - NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
HARSCO Industrial, Patterson-Kelley
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-4247
Unit Identification (Boiler)
| Model | W2000-MFD | Year Built | 2016
| Nat. Bd. # | XXXX |  | CSA Report # |  | 166908-1612096
| Boiler/Burner Serial Number |  |  | XXYY-16-ZZZZZ
| Jurisdiction |  | ILLINOIS
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 2000000 | btu/hr
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Copper, Watertube
| Boiler Unit Capacity (Output) |  |  |  |  | 1700000 | btu/hr
| Burner Manufacturer |  |  | HARSCO Industrial / Patterson-Kelley Co.
| Model | W2000-MFD |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | EXAMPLE BUILDING
| Adress |  | 123 MAIN ST
| City | SPRINGFIELD |  | State | IL | Zip | 62701
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  | (self contained) | Honeywell |  | RM7910A1183/U
Safety Controls
L.W.C.O., Forced Circulation - CW210 |  |  |  | Johnson |  | F261KAH-V01C
High Water Temperature Limit - CW-410(b) |  |  |  | Jumo |  | EMF-5
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_2500/602_S02
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_2500/602_S02
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.E021180
High Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Low Gas Pressure - CF162 |  |  |  | Honeywell |  | C6097A1004
Purge Air Flow - CF210 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | RM7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | C7027A1114(UV)
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20 | (3/4"x 3/4")
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | P-K REP CO.
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | XXYY-16-ZZZZZ