## INSTRUCTIONS
PATTERSON - KELLEY, LLC CSD-1 FORM
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
1 | Complete data below
| a. | from the packing list, enter the serial number
| b. | from the serial number, enter the year built
(e.g. - ST300-17-00506 means year built is 2017)
2 | Enter Jurisdiction (usually the state)
3 | Enter installation information
Name
Address
City
State
Zip
Phone
Fax
4 | Enter Representative's Company name
5 | IMPORTANT: Select correct tab (below) for correct model number
6 | The cell for the fuels (as shipped) is NOT locked so that you can enter this information.
7 | The cells for the relief valve are NOT locked so that you can correct for the supplied valve.
8 | Print the "worksheet" for that model ONLY.
This workbook will populate ALL models and ALL tabs with the same information - again, only select
and print the worksheet for your specific model.

## SOLIS SL-725 NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
Patterson-Kelley, LLC
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-7247
Unit Identification (Boiler)
| Model | SL-1500 | Year Built | 0
| CSA Report # |  | 80068761
| Boiler/Burner Serial Number |  |  | 0
| Jurisdiction |  | 0
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 1500000 | btu
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Stainless Steel, Firetube
| Boiler Unit Capacity (Output) |  |  |  |  | 1440000 | btu/hr
| Burner Manufacturer |  |  | Patterson-Kelley, LLC
| Model | SL-1500 |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | 0
| Adress |  | 0
| City | 0 |  | State | 0 | Zip | 0
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  |  | Honeywell |  | R7910A1183/U
Safety Controls
L.W.C.O., Probe - CW210 |  |  |  | Tasseron |  | TSL050C
High Water Temperature Limit - CW-410(b) |  |  |  | JUMO |  | EM-50
(200°F Max)
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.S020180
High Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4516-4012
Low Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4515-4011
Purge Air Flow - CF210 |  |  |  | Honeywell |  | R7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20
|  | Size |  |  |  | (3/4"x 3/4")
|  | Pressure Setting |  |  |  | 100#
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | 0
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | 0

## SOLIS SL-850 NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
Patterson-Kelley, LLC
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-7247
Unit Identification (Boiler)
| Model | SL-850 | Year Built | 0
| CSA Report # |  | 80068761
| Boiler/Burner Serial Number |  |  | 0
| Jurisdiction |  | 0
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 850000 | btu
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Stainless Steel, Firetube
| Boiler Unit Capacity (Output) |  |  |  |  | 829000 | btu/hr
| Burner Manufacturer |  |  | Patterson-Kelley, LLC
| Model | SL-850 |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | 0
| Adress |  | 0
| City | 0 |  | State | 0 | Zip | 0
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  |  | Honeywell |  | R7910A1183/U
Safety Controls
L.W.C.O., Probe - CW210 |  |  |  | Tasseron |  | TSL050C
High Water Temperature Limit - CW-410(b) |  |  |  | JUMO |  | EM-50
(200°F Max)
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.S020180
High Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4516-4012
Low Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4515-4011
Purge Air Flow - CF210 |  |  |  | Honeywell |  | R7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20
|  | Size |  |  |  | (3/4"x 3/4")
|  | Pressure Setting |  |  |  | 100#
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | 0
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | 0

## SOLIS SL-1000 NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
Patterson-Kelley, LLC
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-7247
Unit Identification (Boiler)
| Model | SL-1000 | Year Built | 0
| CSA Report # |  | 80068761
| Boiler/Burner Serial Number |  |  | 0
| Jurisdiction |  | 0
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 1000000 | btu
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Stainless Steel, Firetube
| Boiler Unit Capacity (Output) |  |  |  |  | 965000 | btu/hr
| Burner Manufacturer |  |  | Patterson-Kelley, LLC
| Model | SL-1000 |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | 0
| Adress |  | 0
| City | 0 |  | State | 0 | Zip | 0
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  |  | Honeywell |  | R7910A1183/U
Safety Controls
L.W.C.O., Probe - CW210 |  |  |  | Tasseron |  | TSL050C
High Water Temperature Limit - CW-410(b) |  |  |  | JUMO |  | EM-50
(200°F Max)
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000,P/N257-805
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE_1000,P/N257-805
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.S020180
High Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4516-4012
Low Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4515-4011
Purge Air Flow - CF210 |  |  |  | Honeywell |  | R7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20
|  | Size |  |  |  | (3/4"x 3/4")
|  | Pressure Setting |  |  |  | 100#
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | 0
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | 0

## SOLIS SL-1500 NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
Patterson-Kelley, LLC
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-7247
Unit Identification (Boiler)
| Model | SL-1500 | Year Built | 0
| CSA Report # |  | 80068761
| Boiler/Burner Serial Number |  |  | 0
| Jurisdiction |  | 0
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 1500000 | btu
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Stainless Steel, Firetube
| Boiler Unit Capacity (Output) |  |  |  |  | 1440000 | btu/hr
| Burner Manufacturer |  |  | Patterson-Kelley, LLC
| Model | SL-1500 |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | 0
| Adress |  | 0
| City | 0 |  | State | 0 | Zip | 0
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  |  | Honeywell |  | R7910A1183/U
Safety Controls
L.W.C.O., Probe - CW210 |  |  |  | Tasseron |  | TSL050C
High Water Temperature Limit - CW-410(b) |  |  |  | JUMO |  | EM-50
(200°F Max)
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.S020180
High Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4516-4012
Low Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4515-4011
Purge Air Flow - CF210 |  |  |  | Honeywell |  | R7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20
|  | Size |  |  |  | (3/4"x 3/4")
|  | Pressure Setting |  |  |  | 100#
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | 0
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | 0

## SOLIS SL-2000 NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
Patterson-Kelley, LLC
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-7247
Unit Identification (Boiler)
| Model | SL-2000 | Year Built | 0
| CSA Report # |  | 80068761
| Boiler/Burner Serial Number |  |  | 0
| Jurisdiction |  | 0
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 2000000 | btu
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Stainless Steel, Firetube
| Boiler Unit Capacity (Output) |  |  |  |  | 1920000 | btu/hr
| Burner Manufacturer |  |  | Patterson-Kelley, LLC
| Model | SL-2000 |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | 0
| Adress |  | 0
| City | 0 |  | State | 0 | Zip | 0
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  |  | Honeywell |  | R7910A1183/U
Safety Controls
L.W.C.O., Probe - CW210 |  |  |  | Tasseron |  | TSL050C
High Water Temperature Limit - CW-410(b) |  |  |  | JUMO |  | EM-50
(200°F Max)
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBC-SE-2500/602-S02
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.S020180
High Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4516-4012
Low Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4515-4011
Purge Air Flow - CF210 |  |  |  | Honeywell |  | R7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-604-20
|  | Size |  |  |  | (3/4"x 3/4")
|  | Pressure Setting |  |  |  | 100#
|  | Capacity |  |  |  | 2162000 | btu/hr
Representing Equipment Manufacturer
Name | 0
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | 0

## SOLIS SL-2500 NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
Patterson-Kelley, LLC
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-7247
Unit Identification (Boiler)
| Model | SL-2500 | Year Built | 0
| CSA Report # |  | 80068761
| Boiler/Burner Serial Number |  |  | 0
| Jurisdiction |  | 0
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 2500000 | btu
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Stainless Steel, Firetube
| Boiler Unit Capacity (Output) |  |  |  |  | 2400000 | btu/hr
| Burner Manufacturer |  |  | Patterson-Kelley, LLC
| Model | SL-2500 |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | 0
| Adress |  | 0
| City | 0 |  | State | 0 | Zip | 0
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  |  | Honeywell |  | R7910A1183/U
Safety Controls
L.W.C.O., Probe - CW210 |  |  |  | Tasseron |  | TSL050C
High Water Temperature Limit - CW-410(b) |  |  |  | JUMO |  | EM-50
(200°F Max)
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBE-2L
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBE-2L
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.S020180
High Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4516-4012
Low Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4515-4011
Purge Air Flow - CF210 |  |  |  | Honeywell |  | R7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-605-34
|  | Size |  |  |  | (1"x 1")
|  | Pressure Setting |  |  |  | 100#
|  | Capacity |  |  |  | 3500000 | btu/hr
Representing Equipment Manufacturer
Name | 0
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | 0

## SOLIS SL-3000 NURO
MANUFACTURER'S / INSTALLING CONTRACTOR'S REPORT FOR ASME CSD-1
Unit Manufacturer
Patterson-Kelley, LLC
155 Burson St.
East Stoudsburg, PA 18301
ph- 570-421-7500 fax- 570-476-7247
Unit Identification (Boiler)
| Model | SL-3000 | Year Built | 0
| CSA Report # |  | 80068761
| Boiler/Burner Serial Number |  |  | 0
| Jurisdiction |  | 0
Hot Water
| Max. W.P. | 160 | psig | Max. Temp. |  | 210 | ˚F
| Min. Safety Relief Valve Capacity |  |  |  |  | 4000000 | btu
| Boiler Unit Description (Type) |  |  | Gas Fired, Forced Circulation, Stainless Steel, Firetube
| Boiler Unit Capacity (Output) |  |  |  |  | 2880000 | btu/hr
| Burner Manufacturer |  |  | Patterson-Kelley, LLC
| Model | SL-3000 |  | Fuels (as shipped) |  | Natural Gas
Installation Location
| Customer Name |  | 0
| Adress |  | 0
| City | 0 |  | State | 0 | Zip | 0
| Phone | 0 |  | Fax |  | 0
Installer Operational
Control / Device |  |  |  | Manufacturer |  | Model # |  | Test Performed, Date
Operating Controls
Water Temperature - CW410(b) |  |  |  | Honeywell |  | R7910A1183/U
Safety Controls
L.W.C.O., Probe - CW210 |  |  |  | Tasseron |  | TSL050C
High Water Temperature Limit - CW-410(b) |  |  |  | JUMO |  | EM-50
(200°F Max)
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBE-2L
Fuel Safety Shutoff Valve - CF180(b)(1) |  |  |  | Dungs |  | MBE-2L
Combustion Air Switch - CF220 |  |  |  | HUBA |  | 604.S020180
High Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4516-4012
Low Gas Pressure - CF162 |  |  |  | Tecmark |  | GFS4515-4011
Purge Air Flow - CF210 |  |  |  | Honeywell |  | R7910A1183/U
Flame Safeguard (Primary) - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Flame Detector - CF310/320 |  |  |  | Honeywell |  | R7910A1183/U
Safety Relief Valve - CW510 |  |  |  | Conbraco |  | 10-605-34
|  | Size |  |  |  | (1"x 1")
|  | Pressure Setting |  |  |  | 100#
|  | Capacity |  |  |  | 3500000 | btu/hr
Representing Equipment Manufacturer
Name | 0
Signature | [5 empty] | Date
Representing Installing Contractor
Name
Signature | [5 empty] | Date
[6 empty] | Serial No. | 0