## Schedule Tool
Multiple boilers: |  |  |  | Changing the boiler:
1. If more than one row is required, copy the entire row 7 by right clicking on 7 and then copy |  |  |  | 1. Click on the blue cell below "Model" a drop down menu will appear and you can select which PK boiler you need
2. Right click on row 8 and choose "Insert Copied Cells"
Boiler Schedule
[6 empty] | Burner data | [7 empty] | Electrical Data |  | Water Data |  |  |  | Boiler Data
| Boiler # | Location | Manufacturer | Model | Boiler type | BTU Input | Max BTU Output | Min BTU Input | Min BTU Output | Efficiency | Turndown Ratio | Gas pressure range | Fuel | Electrical Requirements | Operating current | RV opening size | Max boiler PSI | Water capacity | Min/Max flow GPM | Operating weight | Dimensions
|  |  | Patterson-Kelley, LLC | SC-650 LP | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Notes
| 1. NURO controller required |  |  |  |  | 9. Minimum efficiency of 94.1%
| 2. Boiler must control pump and modulate based on firing rate |  |  |  |  | 10. Boiler must be BMS capable
| 3. Venting system must be engineered to manufacturers pressure specifications |  |  |  |  | 11. Gas inlet pressure range of 7-14" W.C.
4. Gas line must be sized for less than a 2" W.C. pressure drop
5. Water quality to be maintained to manufacturers specifications
6. Mechanical Turndown required
7. Cascaded boilers must have a designated fail safe program if communication with master is lost
8. Minimum turndown of 5.2:1

## Data (hidden)
Boiler Schedule Example
Boiler # | Manufacturer | Model | BTU Input | Max BTU Output | Min BTU Input | Min BTU Output | Electrical Requirements | RV opening size | Efficiency | Turndown | Water capacity | Gas pressure range | Operating weight | Dimensions | Boiler type | Max boiler pressure | Operating current | Fuel | Min/Max water flow GPM
B-1 | Patterson-Kelley | SC-650 Dual Fuel | 650000 | 611650 | 125000 | 117625 | 120V 1PH 60Hz | 1" | 94.1 | 5.2:1 | <10 Gallons | 3.5-14" W.C. | 830 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | NG or LP | 25/62
B-1 | Patterson-Kelley | SC-650 NG | 650000 | 611650 | 125000 | 117625 | 120V 1PH 60Hz | 1" | 94.1 | 5.2:1 | <10 Gallons | 3.5-14" W.C. | 780 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | NG | 25/62
B-1 | Patterson-Kelley | SC-650 LP | 650000 | 611650 | 125000 | 117625 | 120V 1PH 60Hz | 1" | 94.1 | 5.2:1 | <10 Gallons | 7-14" W.C. | 780 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | LP | 25/62
B-1 | Patterson-Kelley | SC-750 Dual Fuel | 750000 | 705750 | 125000 | 117625 | 120V 1PH 60Hz | 1" | 94.1 | 6:1 | <10 Gallons | 3.5-14" W.C. | 830 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | NG or LP | 25/72
B-1 | Patterson-Kelley | SC-750 NG | 750000 | 705750 | 125000 | 117625 | 120V 1PH 60Hz | 1" | 94.1 | 6:1 | <10 Gallons | 3.5-14" W.C. | 780 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | NG | 25/72
B-1 | Patterson-Kelley | SC-750 LP | 750000 | 705750 | 125000 | 117625 | 120V 1PH 60Hz | 1" | 94.1 | 6:1 | <10 Gallons | 7-14" W.C. | 780 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | LP | 25/72
B-1 | Patterson-Kelley | SC-850 Dual Fuel | 850000 | 799850 | 141000 | 132681 | 120V 1PH 60Hz | 1" | 94.1 | 6:1 | <10 Gallons | 3.5-14" W.C. | 850 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | NG or LP | 30/82
B-1 | Patterson-Kelley | SC-850 NG | 850000 | 799850 | 141000 | 132681 | 120V 1PH 60Hz | 1" | 94.1 | 6:1 | <10 Gallons | 3.5-14" W.C. | 800 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | NG | 30/82
B-1 | Patterson-Kelley | SC-850 LP | 850000 | 799850 | 141000 | 132681 | 120V 1PH 60Hz | 1" | 94.1 | 6:1 | <10 Gallons | 7-14" W.C. | 800 lbs | 84x36x57 | Condensing water tube | 160 | < 5 amps | LP | 30/82
B-1 | Patterson-Kelley | SC-1000 Dual Fuel | 1000000 | 923000 | 143000 | 131989 | 120V 1PH 60Hz | 1" | 92.3 | 7:1 | <10 Gallons | 3.5-14" W.C. | 810 lbs | 84x36x57 | Condensing water tube | 160 | <10 amps | NG or LP | 30/92
B-1 | Patterson-Kelley | SC-1000 NG | 1000000 | 923000 | 143000 | 131989 | 120V 1PH 60Hz | 1" | 92.3 | 7:1 | <10 Gallons | 3.5-14" W.C. | 810 lbs | 84x36x57 | Condensing water tube | 160 | <10 amps | NG | 30/92
B-1 | Patterson-Kelley | SC-1000 LP | 1000000 | 923000 | 143000 | 131989 | 120V 1PH 60Hz | 1" | 92.3 | 7:1 | <10 Gallons | 7-14" W.C. | 810 lbs | 84x36x57 | Condensing water tube | 160 | <10 amps | LP | 30/92
B-1 | Patterson-Kelley | SC-1500 Dual Fuel | 1500000 | 1456500 | 291000 | 282561 | 208/240v 1PH 60 Hz | 1" | 97.1 | 5:1 | 23.9 Gallons | 3.5-14" W.C. | 1550 lbs | 36x84x80 | Condensing water tube | 160 | <15 amps | NG or LP | 46/145
B-1 | Patterson-Kelley | SC-1500 NG | 1500000 | 1456500 | 291000 | 282561 | 208/240v 1PH 60 Hz | 1" | 97.1 | 5:1 | 23.9 Gallons | 3.5-14" W.C. | 1450 lbs | 36x84x80 | Condensing water tube | 160 | <15 amps | NG | 46/145
B-1 | Patterson-Kelley | SC-1500 LP | 1500000 | 1456500 | 291000 | 282561 | 208/240v 1PH 60 Hz | 1" | 97.1 | 5:1 | 23.9 Gallons | 7-14" W.C. | 1450 lbs | 36x84x80 | Condensing water tube | 160 | <15 amps | LP | 46/145
B-1 | Patterson-Kelley | SC-2000 Dual Fuel | 2000000 | 1926000 | 384000 | 369792 | 208/240v 1PH 60 Hz | 1" | 96.3 | 5:1 | 23.9 Gallons | 3.5-14" W.C. | 1550 lbs | 36x84x80 | Condensing water tube | 160 | <15 amps | NG or LP | 62/192
B-1 | Patterson-Kelley | SC-2000 NG | 2000000 | 1926000 | 384000 | 369792 | 208/240v 1PH 60 Hz | 1" | 96.3 | 5:1 | 23.9 Gallons | 3.5-14" W.C. | 1450 lbs | 36x84x80 | Condensing water tube | 160 | <15 amps | NG | 62/192
B-1 | Patterson-Kelley | SC-2000 LP | 2000000 | 1926000 | 384000 | 369792 | 208/240v 1PH 60 Hz | 1" | 96.3 | 5:1 | 23.9 Gallons | 7-14" W.C. | 1450 lbs | 36x84x80 | Condensing water tube | 160 | <15 amps | LP | 62/192
B-1 | Patterson-Kelley | SC-3000 Dual Fuel 208-240v | 3000000 | 2907000 | 581400 | 563376.6 | 208/240v 3PH 60 Hz | 1.25" | 96.9 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2145 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG or LP | 93/285
B-1 | Patterson-Kelley | SC-3000 NG 208-240v | 3000000 | 2907000 | 581400 | 563376.6 | 208/240v 3PH 60 Hz | 1.25" | 96.9 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2045 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG | 93/285
B-1 | Patterson-Kelley | SC-3000 LP 208-240v | 3000000 | 2907000 | 581400 | 563376.6 | 208/240v 3PH 60 Hz | 1.25" | 96.9 | 5:1 | 35 Gallons | 7-14" W.C. | 2045 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | LP | 93/285
B-1 | Patterson-Kelley | SC-3000 Dual Fuel 440-480v | 3000000 | 2907000 | 581400 | 563376.6 | 440/480v 3PH 60Hz | 1.25" | 96.9 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2145 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG or LP | 93/285
B-1 | Patterson-Kelley | SC-3000 NG 440-480v | 3000000 | 2907000 | 581400 | 563376.6 | 440/480v 3PH 60Hz | 1.25" | 96.9 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2045 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG | 93/285
B-1 | Patterson-Kelley | SC-3000 LP 440-480v | 3000000 | 2907000 | 581400 | 563376.6 | 440/480v 3PH 60Hz | 1.25" | 96.9 | 5:1 | 35 Gallons | 7-14" W.C. | 2045 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | LP | 93/285
B-1 | Patterson-Kelley | SC-4000 Dual Fuel 208-240v | 4000000 | 3840000 | 768000 | 737280 | 208/240v 3PH 60 Hz | 1.25" | 96 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2195 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG or LP | 125/384
B-1 | Patterson-Kelley | SC-4000 NG 208-240v | 4000000 | 3840000 | 768000 | 737280 | 208/240v 3PH 60 Hz | 1.25" | 96 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2095 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG | 125/384
B-1 | Patterson-Kelley | SC-4000 LP 208-240v | 4000000 | 3840000 | 768000 | 737280 | 208/240v 3PH 60 Hz | 1.25" | 96 | 5:1 | 35 Gallons | 7-14" W.C. | 2095 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | LP | 125/384
B-1 | Patterson-Kelley | SC-4000 Dual Fuel 440-480v | 4000000 | 3840000 | 768000 | 737280 | 440/480v 3PH 60Hz | 1.25" | 96 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2195 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG or LP | 125/384
B-1 | Patterson-Kelley | SC-4000 NG 440-480v | 4000000 | 3840000 | 768000 | 737280 | 440/480v 3PH 60Hz | 1.25" | 96 | 5:1 | 35 Gallons | 3.5-14" W.C. | 2095 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | NG | 125/384
B-1 | Patterson-Kelley | SC-4000 LP 440-480v | 4000000 | 3840000 | 768000 | 737280 | 440/480v 3PH 60Hz | 1.25" | 96 | 5:1 | 35 Gallons | 7-14" W.C. | 2095 lbs | 36x84x80 | Condensing water tube | 160 | <20 amps | LP | 125/384
B-1 | Patterson-Kelley | CM-300 NG | 300000 | 279000 | 60000 | 55800 | 120V 1PH 60Hz | 3/4" | 93 | 5:1 | 1.2 Gallons | 3.5-14" W.C. | 420 lbs | 58x38x63 | Condensing water tube | 80 | <5 amps | NG | 6/28
B-1 | Patterson-Kelley | CM-300 LP | 300000 | 279000 | 60000 | 55800 | 120V 1PH 60Hz | 3/4" | 93 | 5:1 | 1.2 Gallons | 7-14" W.C. | 420 lbs | 58x38x63 | Condensing water tube | 80 | <5 amps | LP | 6/28
B-1 | Patterson-Kelley | CM-399 NG | 399000 | 371070 | 79800 | 74214 | 120V 1PH 60Hz | 3/4" | 93 | 5:1 | 1.58 Gallons | 3.5-14" W.C. | 402 lbs | 53x29x60 | Condensing water tube | 80 | <5 amps | NG | 7/37
B-1 | Patterson-Kelley | CM-399 LP | 399000 | 371070 | 79800 | 74214 | 120V 1PH 60Hz | 3/4" | 93 | 5:1 | 1.58 Gallons | 7-14" W.C. | 402 lbs | 53x29x60 | Condensing water tube | 80 | <5 amps | LP | 7/37
B-1 | Patterson-Kelley | CM-500 NG | 500000 | 456000 | 100000 | 91200 | 120V 1PH 60Hz | 3/4" | 91.2 | 5:1 | 1.58 Gallons | 3.5-14" W.C. | 440 lbs | 53x29x60 | Condensing water tube | 80 | <5 amps | NG | 9/46
B-1 | Patterson-Kelley | CM-500 LP | 500000 | 456000 | 100000 | 91200 | 120V 1PH 60Hz | 3/4" | 91.2 | 5:1 | 1.58 Gallons | 7-14" W.C. | 440 lbs | 53x29x60 | Condensing water tube | 80 | <5 amps | LP | 9/46
B-1 | Patterson-Kelley | C-750 Dual Fuel | 750000 | 704010 | 150000 | 140802 | 120V 1PH 60Hz | 1" | 93.868 | 5:1 | 5.9 Gallons | 3.5-14" W.C. | 695 lbs | 60x36x60 | Condensing water tube | 80 | <6 amps | NG or LP | 14/75
B-1 | Patterson-Kelley | C-750 NG | 750000 | 704010 | 75000 | 70401 | 120V 1PH 60Hz | 1" | 93.868 | 10:1 | 5.9 Gallons | 3.5-14" W.C. | 695 lbs | 60x36x60 | Condensing water tube | 80 | <6 amps | NG | 14/75
B-1 | Patterson-Kelley | C-750 LP | 750000 | 704010 | 150000 | 140802 | 120V 1PH 60Hz | 1" | 93.868 | 5:1 | 5.9 Gallons | 7-14" W.C. | 695 lbs | 60x36x60 | Condensing water tube | 80 | <6 amps | LP | 14/75
B-1 | Patterson-Kelley | C-900 Dual Fuel | 900000 | 845100 | 180000 | 169020 | 120V 1PH 60Hz | 1" | 93.9 | 5:1 | 6.6 Gallons | 3.5-14" W.C. | 735 lbs | 60x36x60 | Condensing water tube | 80 | <6 amps | NG or LP | 17/90
B-1 | Patterson-Kelley | C-900 NG | 900000 | 845100 | 90000 | 84510 | 120V 1PH 60Hz | 1" | 93.9 | 10:1 | 6.6 Gallons | 3.5-14" W.C. | 735 lbs | 60x36x60 | Condensing water tube | 80 | <6 amps | NG | 17/90
B-1 | Patterson-Kelley | C-900 LP | 900000 | 845100 | 180000 | 169020 | 120V 1PH 60Hz | 1" | 93.9 | 5:1 | 6.6 Gallons | 7-14" W.C. | 735 lbs | 60x36x60 | Condensing water tube | 80 | <6 amps | LP | 17/90
B-1 | Patterson-Kelley | C-1050 Dual Fuel | 1050000 | 988050 | 210000 | 197610 | 120V 1PH 60Hz | 1" | 94.1 | 5:1 | 7.3 Gallons | 3.5-14" W.C. | 780 lbs | 60x36x60 | Condensing water tube | 125 | <6 amps | NG or LP | 20/110
B-1 | Patterson-Kelley | C-1050 NG | 1050000 | 988050 | 105000 | 98805 | 120V 1PH 60Hz | 1" | 94.1 | 10:1 | 7.3 Gallons | 3.5-14" W.C. | 780 lbs | 60x36x60 | Condensing water tube | 125 | <6 amps | NG | 20/110
B-1 | Patterson-Kelley | C-1050 LP | 1050000 | 988050 | 210000 | 197610 | 120V 1PH 60Hz | 1" | 94.1 | 5:1 | 7.3 Gallons | 7-14" W.C. | 780 lbs | 60x36x60 | Condensing water tube | 125 | <6 amps | LP | 20/110
B-1 | Patterson-Kelley | C-1500H Dual Fuel | 1500000 | 1411500 | 300000 | 282300 | 120V 1PH 60Hz | 1.25" | 94.1 | 5:1 | 13.2 Gallons | 3.5-14" W.C. | 1300 lbs | 36x84x68 | Condensing water tube | 125 | <15 amps | NG or LP | 28/141
B-1 | Patterson-Kelley | C-1500H NG | 1500000 | 1411500 | 150000 | 141150 | 120V 1PH 60Hz | 1.25" | 94.1 | 10:1 | 13.2 Gallons | 3.5-14" W.C. | 1200 lbs | 36x84x68 | Condensing water tube | 125 | <15 amps | NG | 28/141
B-1 | Patterson-Kelley | C-1500H LP | 1500000 | 1411500 | 300000 | 282300 | 120V 1PH 60Hz | 1.25" | 94.1 | 5:1 | 13.2 Gallons | 7-14" W.C. | 1200 lbs | 36x84x68 | Condensing water tube | 125 | <15 amps | LP | 28/141
B-1 | Patterson-Kelley | C-2000H Dual Fuel | 2000000 | 1846000 | 400000 | 369200 | 120V 1PH 60Hz | 1.25" | 92.3 | 5:1 | 17 Gallons | 3.5-14" W.C. | 1600 lbs | 36x84x68 | Condensing water tube | 125 | <15 amps | NG or LP | 38/188
B-1 | Patterson-Kelley | C-2000H NG | 2000000 | 1846000 | 200000 | 184600 | 120V 1PH 60Hz | 1.25" | 92.3 | 10:1 | 17 Gallons | 3.5-14" W.C. | 1500 lbs | 36x84x68 | Condensing water tube | 125 | <15 amps | NG | 38/188
B-1 | Patterson-Kelley | C-2000H LP | 2000000 | 1846000 | 400000 | 369200 | 120V 1PH 60Hz | 1.25" | 92.3 | 5:1 | 17 Gallons | 7-14" W.C. | 1500 lbs | 36x84x68 | Condensing water tube | 125 | <15 amps | LP | 38/188
B-1 | Patterson-Kelley | C-2500 Dual Fuel | 2500000 | 2352500 | 500000 | 470500 | 120V 1PH 60Hz | 1" | 94.1 | 5:1 | 19 Gallons | 3.5-14" W.C. | 1650 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | NG or LP | 47/238
B-1 | Patterson-Kelley | C-2500 NG | 2500000 | 2352500 | 500000 | 470500 | 120V 1PH 60Hz | 1" | 94.1 | 5:1 | 19 Gallons | 3.5-14" W.C. | 1550 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | NG | 47/238
B-1 | Patterson-Kelley | C-2500 LP | 2500000 | 2352500 | 500000 | 470500 | 120V 1PH 60Hz | 1" | 94.1 | 5:1 | 19 Gallons | 7-14" W.C. | 1550 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | LP | 47/238
B-1 | Patterson-Kelley | C-3000 Dual Fuel 208-240v | 3000000 | 2823000 | 600000 | 564600 | 208/240v 3PH 60 Hz | 1" | 94.1 | 5:1 | 19 Gallons | 3.5-14" W.C. | 1700 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | NG or LP | 57/285
B-1 | Patterson-Kelley | C-3000 NG 208-240v | 3000000 | 2823000 | 600000 | 564600 | 208/240v 3PH 60 Hz | 1" | 94.1 | 5:1 | 19 Gallons | 3.5-14" W.C. | 1600 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | NG | 57/285
B-1 | Patterson-Kelley | C-3000 LP 208-240v | 3000000 | 2823000 | 600000 | 564600 | 208/240v 3PH 60 Hz | 1" | 94.1 | 5:1 | 19 Gallons | 7-14" W.C. | 1600 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | LP | 57/285
B-1 | Patterson-Kelley | C-3000 Dual Fuel 440-480v | 3000000 | 2823000 | 600000 | 564600 | 440/480v 3PH 60Hz | 1" | 94.1 | 5:1 | 19 Gallons | 3.5-14" W.C. | 1700 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | NG or LP | 57/285
B-1 | Patterson-Kelley | C-3000 NG 440-480v | 3000000 | 2823000 | 600000 | 564600 | 440/480v 3PH 60Hz | 1" | 94.1 | 5:1 | 19 Gallons | 3.5-14" W.C. | 1600 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | NG | 57/285
B-1 | Patterson-Kelley | C-3000 LP 440-480v | 3000000 | 2823000 | 600000 | 564600 | 440/480v 3PH 60Hz | 1" | 94.1 | 5:1 | 19 Gallons | 7-14" W.C. | 1600 lbs | 36x84x87 | Condensing water tube | 125 | <15 amps | LP | 57/285
B-1 | Patterson-Kelley | C-4000 Dual Fuel 208-240v | 4000000 | 3764000 | 800000 | 752800 | 208/240v 3PH 60 Hz | 1" | 94.1 | 5:1 | 24.5 Gallons | 3.5-14" W.C. | 1900 lbs | 36x84x87 | Condensing water tube | 125 | <20 amps | NG or LP | 76/380
B-1 | Patterson-Kelley | C-4000 NG 208-240v | 4000000 | 3764000 | 800000 | 752800 | 208/240v 3PH 60 Hz | 1" | 94.1 | 5:1 | 24.5 Gallons | 3.5-14" W.C. | 1900 lbs | 36x84x87 | Condensing water tube | 125 | <20 amps | NG | 76/380
B-1 | Patterson-Kelley | C-4000 LP 208-240v | 4000000 | 3764000 | 800000 | 752800 | 208/240v 3PH 60 Hz | 1" | 94.1 | 5:1 | 24.5 Gallons | 7-14" W.C. | 1900 lbs | 36x84x87 | Condensing water tube | 125 | <20 amps | LP | 76/380
B-1 | Patterson-Kelley | C-4000 Dual Fuel 440-480v | 4000000 | 3764000 | 800000 | 752800 | 440/480v 3PH 60Hz | 1" | 94.1 | 5:1 | 24.5 Gallons | 3.5-14" W.C. | 2000 lbs | 36x84x87 | Condensing water tube | 125 | <20 amps | NG or LP | 76/380
B-1 | Patterson-Kelley | C-4000 NG 440-480v | 4000000 | 3764000 | 800000 | 752800 | 440/480v 3PH 60Hz | 1" | 94.1 | 5:1 | 24.5 Gallons | 3.5-14" W.C. | 1900 lbs | 36x84x87 | Condensing water tube | 125 | <20 amps | NG | 76/380
B-1 | Patterson-Kelley | C-4000 LP 440-480v | 4000000 | 3764000 | 800000 | 752800 | 440/480v 3PH 60Hz | 1" | 94.1 | 5:1 | 24.5 Gallons | 7-14" W.C. | 1900 lbs | 36x84x87 | Condensing water tube | 125 | <20 amps | LP | 76/380
B-1 | Patterson-Kelley | ST-650 | 650000 | 630500 | 65000 | 63050 | 120V 1PH 60Hz | 1" | 97 | 10:1 |  | 3.5-14" W.C. |  |  | Condensing water tube | 160 |  | NG
B-1 | Patterson-Kelley | ST-800 | 800000 | 776000 | 80000 | 77600 | 120V 1PH 60Hz | 1" | 97 | 10:1 |  | 3.5-14" W.C. |  |  | Condensing water tube | 160 |  | NG
B-1 | Patterson-Kelley | ST-1000 | 1000000 | 970000 | 100000 | 97000 | 120V 1PH 60Hz | 1" | 97 | 10:1 |  | 3.5-14" W.C. |  |  | Condensing water tube | 160 |  | NG
B-1 | Patterson-Kelley | ST-1250 | 1250000 | 1212500 | 125000 | 121250 | 208/240v 1PH 60 Hz | 1.25" | 97 | 10:1 | 11 Gallons | 3.5-14" W.C. | 1112 lbs | 72x38x60 | Condensing water tube | 160 | 20 amps | NG | 38/121
B-1 | Patterson-Kelley | ST-1500 | 1500000 | 1455000 | 150000 | 145500 | 208/240v 1PH 60 Hz | 1.25" | 97 | 10:1 | 12.9 Gallons | 3.5-14" W.C. | 1208 lbs | 72x38x60 | Condensing water tube | 160 | 20 amps | NG | 46/146
B-1 | Patterson-Kelley | ST-1750 | 1750000 | 1697500 | 175000 | 169750 | 208/240v 1PH 60 Hz | 1.25" | 97 | 10:1 | 16.2 Gallons | 3.5-14" W.C. | 1305 lbs | 72x38x60 | Condensing water tube | 160 | 20 amps | NG | 54/170
B-1 | Patterson-Kelley | ST-2000 | 2000000 | 1940000 | 200000 | 194000 | 208/240v 1PH 60 Hz | 1.25" | 97 | 10:1 | 16.2 Gallons | 3.5-14" W.C. | 1305 lbs | 72x38x60 | Condensing water tube | 160 | 20 amps | NG | 62/194
B-1 | Patterson-Kelley | ST-2500 | 2500000 | 2425000 | 250000 | 242500 | 208/240v 3PH 60 Hz | 1.25" | 97 | 10:1 | 27 Gallons | 3.5-14" W.C. | 2329 lbs | 79x48x75-5/8 | Condensing water tube | 160 | 20 amps | NG | 69.3/242.5
B-1 | Patterson-Kelley | ST-3000 | 3000000 | 2910000 | 300000 | 291000 | 208/240v 3PH 60 Hz | 1.25" | 97 | 10:1 | 27 Gallons | 3.5-14" W.C. | 2329 lbs | 79x48x75-5/8 | Condensing water tube | 160 | 20 amps | NG | 83/291
B-1 | Patterson-Kelley | ST-3500 | 3500000 | 3395000 | 350000 | 339500 | 440/480v 3PH 60Hz | 1.25" | 97 | 10:1 | 35 Gallons | 3.5-14" W.C. | 2772 lbs | 95x48x75-5/8 | Condensing water tube | 160 | 10 amps | NG | 97/339.5
B-1 | Patterson-Kelley | ST-4000 | 4000000 | 3880000 | 400000 | 388000 | 440/480v 3PH 60Hz | 1.25" | 97 | 10:1 | 35 Gallons | 3.5-14" W.C. | 2772 lbs | 95x48x75-5/8 | Condensing water tube | 160 | 10 amps | NG | 110.9/388
B-1 | Patterson-Kelley | ST-5000 208-240v | 4999999 | 4699999.06 | 499999.9 | 469999.906 | 208/240v 3PH 60 Hz | 1.25" | 94 | 10:1 | 60 Gallons | 3.5-14" W.C. | 3700 lbs | 110x48x80 | Condensing water tube | 160 | 25 amps | NG | 161.7/485
B-1 | Patterson-Kelley | ST-5000 440-480v | 4999999 | 4699999.06 | 499999.9 | 469999.906 | 440/480v 3PH 60Hz | 1.25" | 94 | 10:1 | 60 Gallons | 3.5-14" W.C. | 3700 lbs | 110x48x80 | Condensing water tube | 160 | 15 amps | NG | 161.7/485
B-1 | Patterson-Kelley | ST-6000 208-240v | 6000000 | 5760000 | 600000 | 576000 | 208/240v 3PH 60 Hz | 1.25" | 96 | 10:1 | 60 Gallons | 3.5-14" W.C. | 3700 lbs | 110x48x80 | Condensing water tube | 160 | 25 amps | NG | 194/582
B-1 | Patterson-Kelley | ST-6000 440-480v | 6000000 | 5760000 | 600000 | 576000 | 440/480v 3PH 60Hz | 1.25" | 96 | 10:1 | 60 Gallons | 3.5-14" W.C. | 3700 lbs | 110x48x80 | Condensing water tube | 160 | 15 amps | NG | 194/582
B-1 | Patterson-Kelley | ST-8000 208-240v | 8000000 | 7680000 | 800000 | 768000 | 208/240v 3PH 60 Hz | 1.25" | 96 | 10:1 | 60 Gallons | 3.5-14" W.C. | 3800 lbs | 110x48x80 | Condensing water tube | 160 | 25 amps | NG | 218/764
B-1 | Patterson-Kelley | ST-8000 440-480v | 8000000 | 7680000 | 800000 | 768000 | 440/480v 3PH 60Hz | 1.25" | 96 | 10:1 | 60 Gallons | 3.5-14" W.C. | 3800 lbs | 110x48x80 | Condensing water tube | 160 | 15 amps | NG | 218/764
B-1 | Patterson-Kelley | SL-725 | 725000 | 682225 | 72500 | 68222.5 | 120V 1PH 60Hz | 3/4" | 94.1 | 10:1 | 16.5 Gallons | 3.5-14" W.C. | 669 lbs | 58x34x56 | Condensing fire tube | 160 | <10 amps | NG | 12/
B-1 | Patterson-Kelley | SL-850 | 850000 | 784550 | 85000 | 78455 | 120V 1PH 60Hz | 3/4" | 92.3 | 10:1 | 16.5 Gallons | 3.5-14" W.C. | 669 lbs | 58x34x56 | Condensing fire tube | 160 | <10 amps | NG | 12/
B-1 | Patterson-Kelley | SL-1000 | 1000000 | 941000 | 100000 | 94100 | 120V 1PH 60Hz | 3/4" | 94.1 | 10:1 | 76.8 Gallons | 3.5-14" W.C. | 2150 lbs | 60x32x80 | Condensing fire tube | 160 | <10 amps | NG | 10/96
B-1 | Patterson-Kelley | SL-1500 | 1500000 | 1411500 | 150000 | 141150 | 208/240v 1PH 60 Hz | 3/4" | 94.1 | 10:1 | 117 Gallons | 3.5-14" W.C. | 3000 lbs | 77.3x35x80 | Condensing fire tube | 160 | 15 amps | NG | 20/144
B-1 | Patterson-Kelley | SL-2000 | 2000000 | 1882000 | 200000 | 188200 | 208/240v 1PH 60 Hz | 3/4" | 94.1 | 10:1 | 117 Gallons | 3.5-14" W.C. | 3000 lbs | 77.3x35x80 | Condensing fire tube | 160 | 10 amps | NG | 20/192
B-1 | Patterson-Kelley | SL-2500 | 2500000 | 2352500 | 250000 | 235250 | 208/240v 1PH 60 Hz | 3/4" | 94.1 | 10:1 | 149 Gallons | 3.5-14" W.C. | 3470 lbs | 80x35x80 | Condensing fire tube | 160 | 20 amps | NG | 25/240
B-1 | Patterson-Kelley | SL-3000 208-240v | 3000000 | 2823000 | 300000 | 282300 | 208/240v 3PH 60 Hz | 1" | 94.1 | 10:1 | 149 Gallons | 3.5-14" W.C. | 3470 lbs | 80x35x80 | Condensing fire tube | 160 | 20 amps | NG | 25/288
B-1 | Patterson-Kelley | SL-3000 440-480v | 3000000 | 2823000 | 300000 | 282300 | 440/480v 3PH 60Hz | 1" | 94.1 | 10:1 | 149 Gallons | 3.5-14" W.C. | 3470 lbs | 80x35x80 | Condensing fire tube | 160 | 20 amps | NG | 20/288
-----------------------------------
B-1 | Patterson-Kelley | N-750VX | 750000 | 638000 | 622500 | 531454 | 120V 1PH 60Hz |  | 85.0667 | 1.2:1 | 6.2 Gallons | 3.5-14" W.C. | 800 lbs | 54x32x52 | Non Condensing boiler | 160 | <10 amps | NG | 60/120
B-1 | Patterson-Kelley | N-1000VX | 1000000 | 850000 | 830000 | 708050 | 120V 1PH 60Hz |  | 85 | 1.2:1 | 6.2 Gallons | 3.5-14" W.C. | 800 lbs | 54x32x52 | Non Condensing boiler | 160 | <10 amps | NG | 60/120
B-1 | Patterson-Kelley | N-1500VX | 1500000 | 1260000 | 1245000 | 1045800 | 120V 1PH 60Hz |  | 84 | 1.2:1 | 7.3 Gallons | 3.5-14" W.C. | 985 lbs | 54x32x68 | Non Condensing boiler | 160 | <10 amps | NG | 80/150
B-1 | Patterson-Kelley | N-2000VX | 2000000 | 1680000 | 1660000 | 1394400 | 120V 1PH 60Hz |  | 84 | 1.2:1 | 7.3 Gallons | 3.5-14" W.C. | 986 lbs | 54x32x69 | Non Condensing boiler | 160 | <10 amps | NG | 90/150
B-1 | Patterson-Kelley | N-750 MFD NG | 750000 | 637500 | 150000 | 127500 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 6.2 Gallons | 3.5-14" W.C. | 986 lbs | 54x32x52 | Non Condensing boiler | 160 | <6 amps | NG | 60/120
B-1 | Patterson-Kelley | N-750 MFD LP | 750000 | 637500 | 150000 | 127500 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 6.2 Gallons | 7-14" W.C. | 986 lbs | 54x32x52 | Non Condensing boiler | 160 | <6 amps | LP | 60/120
B-1 | Patterson-Kelley | N-1000 MFD NG | 1000000 | 850000 | 166000 | 141100 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 6.2 Gallons | 3.5-14" W.C. | 986 lbs | 54x32x52 | Non Condensing boiler | 160 | <6 amps | NG | 80/150
B-1 | Patterson-Kelley | N-1000 MFD LP | 1000000 | 850000 | 166000 | 141100 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 6.2 Gallons | 7-14" W.C. | 986 lbs | 54x32x52 | Non Condensing boiler | 160 | <6 amps | LP | 80/150
B-1 | Patterson-Kelley | N-1500 MFD NG | 1500000 | 1275000 | 300000 | 255000 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 7.3 Gallons | 3.5-14" W.C. | 985 lbs | 54x32x68 | Non Condensing boiler | 160 | <10 amps | NG | 90/150
B-1 | Patterson-Kelley | N-1500 MFD LP | 1500000 | 1275000 | 300000 | 255000 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 7.3 Gallons | 7-14" W.C. | 985 lbs | 54x32x68 | Non Condensing boiler | 160 | <10 amps | LP | 90/150
B-1 | Patterson-Kelley | N-2000 MFD NG | 2000000 | 1700000 | 400000 | 340000 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 7.3 Gallons | 3.5-14" W.C. | 985 lbs | 54x32x68 | Non Condensing boiler | 160 | <10 amps | NG | 120/180
B-1 | Patterson-Kelley | N-2000 MFD LP | 2000000 | 1700000 | 400000 | 340000 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 7.3 Gallons | 7-14" W.C. | 985 lbs | 54x32x68 | Non Condensing boiler | 160 | <10 amps | LP | 120/180
B-1 | Patterson-Kelley | N-2500 MFD NG | 2500000 | 2125000 | 500000 | 425000 | 208/240v 1PH 60 Hz |  | 85 | 5:1 | 12.6 Gallons | 4-14" W.C. | 1185 lbs | 54x32x68 | Non Condensing boiler | 160 | <15 amps | NG | 165/270
B-1 | Patterson-Kelley | N-3000 MFD NG | 3000000 | 2550000 | 500010 | 425008.5 | 208/240v 1PH 60 Hz |  | 85 | 6:1 | 12.6 Gallons | 4-14" W.C. | 1187 lbs | 54x32x70 | Non Condensing boiler | 160 | <15 amps | NG | 165/325
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley
B-1 | Patterson-Kelley